## Data center configuration
Data center configuration | Parameters
Server Room Dimensions | 25m×12m×5.4m
Air Supply Method | In-row Cooling
Rack Quantity | 73
Air-Conditioner Quantity | 47
Number of Sensors | 8
Rack Power Range | 25-40kW
Supply Air Temperature Range | 19-22℃
In-Row Cooling Unit Fan Speed | 100%
Aisle Containment Type | Cold Aisle Containment
Sensor Locations | Cold Aisle Containment Front and Rear Doors
Sensor Installation Height | 2.5 m above the floor

## Measured Data
Case | Sensor Measurement Points | Measured Data(℃) | Sensor Locations | Sensor Installation Height
Case 1 | Sensor 1 | 19.01 | Rack Row 1 - Cold Aisle Front Door | Cold Aisle Front Door, 2.5m above the floor
| Sensor 2 | 19.44 | Rack Row 1 - Cold Aisle Rear Door | Cold Aisle Rear Door, 2.5m above the floor
Case 2 | Sensor 1 | 19.89 | Rack Row 1 - Cold Aisle Front Door | Cold Aisle Front Door, 2.5m above the floor
| Sensor 2 | 20.59 | Rack Row 1 - Cold Aisle Rear Door | Cold Aisle Rear Door, 2.5m above the floor
Case 3 | Sensor 1 | 21.37 | Rack Row 1 - Cold Aisle Front Door | Cold Aisle Front Door, 2.5m above the floor
| Sensor 2 | 22.16 | Rack Row 1 - Cold Aisle Rear Door | Cold Aisle Rear Door, 2.5m above the floor
Case 4 | Sensor 1 | 21.84 | Rack Row 1 - Cold Aisle Front Door | Cold Aisle Front Door, 2.5m above the floor
| Sensor 2 | 21.56 | Rack Row 1 - Cold Aisle Rear Door | Cold Aisle Rear Door, 2.5m above the floor
Case 5 | Sensor 1 | 22.51 | Rack Row 1 - Cold Aisle Front Door | Cold Aisle Front Door, 2.5m above the floor
| Sensor 2 | 20.73 | Rack Row 1 - Cold Aisle Rear Door | Cold Aisle Rear Door, 2.5m above the floor
Case 6 | Sensor 1 | 22.16 | Rack Row 1 - Cold Aisle Front Door | Cold Aisle Front Door, 2.5m above the floor
| Sensor 2 | 22.46 | Rack Row 1 - Cold Aisle Rear Door | Cold Aisle Rear Door, 2.5m above the floor